## Cover
CICAT Assessment of AP1000 Safety Systems
AP1000 Infrastructure Model
The MITRE Corporation
2020-05-20
Version 1.2
© 2020 The MITRE Corporation. All rights reserved.
Approved for Public Release: Case #20-1395.

## Modeled Systems
Modeled Systems |  | Level | Safety System | I&C | Automated Capabilities
CNS | Containment System | 1 | X
PCS | Passive Containment Cooling System | 1 | X
PMS | Protection and Safety Monitoring System | 1 | X
PXS | Passive Core Cooling System | 1 | X
SGS | Steam Generator System | 1 | X
VES | Main Control Room Emergency Habitability System | 1 | X
DAS | Diverse Actuation system | 2 | X |  | Reactor and Turbine Trip
PLS | Plant Control System | 2 | X |  | Reactor Regulation
RCS | Reactor Coolant System | 2 | X |  | Automatic Depressurization
DDS | Data Display and Processing System | 3 |  | X
DHS | Data Historian System | 3 |  | X
OCS | Operation and Control Centers System | 3 |  | X
PSS | Physical Security System | 3 |  |  | Alarm failure detection

## CAPABILITY
CAPABILITYNAME | DESCRIPTION | CRITICALITY
CONFINEMENT OF RADIOACTIVE MATERIALS |  | cap MC
CONTROL OF REACTIVITY |  | cap MC
HEAT MANAGEMENT |  | cap MC
Enables and protects plant operators |  | cap MC
Automated system response |  | cap MC
Network connectivity |  | cap ME

## FUNCTION
FUNCTIONNAME | DESCRIPTION | CAPABILITYNAME | CRITICALITY
Actuates safety functions to achieve safe shutdown |  | CONTROL OF REACTIVITY | fx MC
Actuates safety functions to achieve safe shutdown |  | HEAT MANAGEMENT | fx MC
Actuates safety functions to achieve safe shutdown |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Delivers water from PCCWST to containment vessel |  | HEAT MANAGEMENT | fx MC
Detects intruders |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Displays plant data |  | CONTROL OF REACTIVITY | fx ME
Displays plant data |  | HEAT MANAGEMENT | fx ME
Displays plant data |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx ME
Displays safety information |  | CONTROL OF REACTIVITY | fx MS
Displays safety information |  | HEAT MANAGEMENT | fx MS
Displays safety information |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MS
Drains excess water from outside containment vessel |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Emergency Boration |  | CONTROL OF REACTIVITY | fx MC
Enables manual control of non-safety functions |  | CONTROL OF REACTIVITY | fx MC
Enables manual control of non-safety functions |  | HEAT MANAGEMENT | fx MC
Enables manual control of non-safety functions |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Enforces physical access controls |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Initiates automatic reactor trip |  | CONTROL OF REACTIVITY | fx MC
Limits steam generator blowdown during DBEs |  | HEAT MANAGEMENT | fx MC
Maintains positive pressure in MCR |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Monitors plant safety during DBEs |  | CONTROL OF REACTIVITY | fx MC
Monitors plant safety during DBEs |  | HEAT MANAGEMENT | fx MC
Monitors plant safety during DBEs |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Notifies plant operations and law enforcement |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Performs analysis of plant data |  | CONTROL OF REACTIVITY | fx MS
Performs analysis of plant data |  | HEAT MANAGEMENT | fx MS
Performs analysis of plant data |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MS
Performs automatic actuation of non-safety functions |  | CONTROL OF REACTIVITY | fx MC
Performs automatic actuation of non-safety functions |  | HEAT MANAGEMENT | fx MC
Performs automatic actuation of non-safety functions |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Performs automatic actuation of safety functions |  | CONTROL OF REACTIVITY | fx MC
Performs automatic actuation of safety functions |  | HEAT MANAGEMENT | fx MC
Performs automatic actuation of safety functions |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Performs data logging |  | CONTROL OF REACTIVITY | fx MS
Performs data logging |  | HEAT MANAGEMENT | fx MS
Performs data logging |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MS
Provides air flow over containment vessel |  | HEAT MANAGEMENT | fx MC
Provides automatic depressurization |  | HEAT MANAGEMENT | fx MC
Provides automatic reactor trip |  | CONTROL OF REACTIVITY | fx MC
Provides breathable air to MCR |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Provides containment isolation and boundary integrity |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Provides control interfaces |  | CONTROL OF REACTIVITY | fx MC
Provides control interfaces |  | HEAT MANAGEMENT | fx MC
Provides control interfaces |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Provides detection of off-nominal conditions |  | CONTROL OF REACTIVITY | fx MC
Provides detection of off-nominal conditions |  | HEAT MANAGEMENT | fx MC
Provides detection of off-nominal conditions |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Provides display data to MCR |  | CONTROL OF REACTIVITY | fx ME
Provides display data to MCR |  | HEAT MANAGEMENT | fx ME
Provides display data to MCR |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx ME
Provides emergency letdown |  | HEAT MANAGEMENT | fx MC
Provides heat removal during design basis event |  | HEAT MANAGEMENT | fx MC
Provides heat removal for RCS |  | HEAT MANAGEMENT | fx MC
Provides manual reactor trip and safety system actuation |  | CONTROL OF REACTIVITY | fx MC
Provides overpressure protection |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Provides overspeed protection |  | HEAT MANAGEMENT | fx MC
Provides passive recirculation flow within MCR |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Provides path for water makeup to PCCWST |  | HEAT MANAGEMENT | fx MC
Provides path for water makeup to spent fuel pool |  | HEAT MANAGEMENT | fx MC
Provides pH adjustment during DBEs |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Provides remote operation of valves |  | CONTROL OF REACTIVITY | fx MC
Provides remote operation of valves |  | HEAT MANAGEMENT | fx MC
Provides remote operation of valves |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MC
Provides storage and retrieval of historical data |  | CONTROL OF REACTIVITY | fx MS
Provides storage and retrieval of historical data |  | HEAT MANAGEMENT | fx MS
Provides storage and retrieval of historical data |  | CONFINEMENT OF RADIOACTIVE MATERIALS | fx MS
Restricts feedwater flow to steam generator during DBEs |  | HEAT MANAGEMENT | fx MC
Supports manual initiation of reactor trip |  | CONTROL OF REACTIVITY | fx ME
Supports RCS during DBEs |  | HEAT MANAGEMENT | fx MC
Wets exterior of containment vessel |  | HEAT MANAGEMENT | fx MC
Provides flow coastdown on loss of power |  | HEAT MANAGEMENT | fx ME
Sounds alarms, provides visual alerts |  | Enables and protects plant operators | fx MC
Provides display data to MCR |  | Enables and protects plant operators | fx MC
Displays plant data |  | Enables and protects plant operators | fx ME
Performs analysis of plant data |  | Enables and protects plant operators | fx MS
Performs data logging |  | Enables and protects plant operators | fx ME
Provides storage and retrieval of historical data |  | Enables and protects plant operators | fx MC
Displays safety information |  | Enables and protects plant operators | fx MC
Provides remote operation of valves |  | Enables and protects plant operators | fx MC
Detects intruders |  | Enables and protects plant operators | fx MC
Notifies plant operations and law enforcement |  | Enables and protects plant operators | fx MC
Provides control interfaces |  | Enables and protects plant operators | fx ME
Performs automatic actuation of non-safety functions |  | Automated system response | fx MC
Provides path for water makeup to PCCWST |  | Automated system response | fx ME
Provides path for water makeup to spent fuel pool |  | Automated system response | fx ME
Enforces physical access controls |  | Automated system response | fx MC
Enables manual control of non-safety functions |  | Automated system response | fx MC
Performs automatic actuation of safety functions |  | Automated system response | fx MC
Provides detection of off-nominal conditions |  | Automated system response | fx MC
Monitors plant safety during DBEs |  | Automated system response | fx MC
Provides network connectivity |  | Network connectivity | fx ME
Provides access |  | Network connectivity | fx ME
Enforce network segmentation |  | Network connectivity | fx ME

## FSMAP
FUNCTIONNAME | SYSTEMNAME
Actuates safety functions to achieve safe shutdown | PMS
Delivers water from PCCWST to containment vessel | PCS
Detects intruders | PSS
Displays plant data | DDS
Displays safety information | OCS
Drains excess water from outside containment vessel | PCS
Emergency Boration | PXS
Enables manual control of non-safety functions | PLS
Enforces physical access controls | PSS
Initiates automatic reactor trip | PMS
Limits steam generator blowdown during DBEs | SGS
Maintains positive pressure in MCR | VES
Monitors plant safety during DBEs | PMS
Notifies plant operations and law enforcement | PSS
Performs analysis of plant data | DDS
Performs automatic actuation of non-safety functions | DAS
Performs automatic actuation of non-safety functions | PLS
Performs automatic actuation of safety functions | PMS
Performs data logging | DHS
Provides air flow over containment vessel | PCS
Provides automatic depressurization | RCS
Provides automatic reactor trip | DAS
Provides breathable air to MCR | VES
Provides containment isolation and boundary integrity | CNS
Provides containment isolation and boundary integrity | PXS
Provides containment isolation and boundary integrity | SGS
Provides control interfaces | PLS
Provides detection of off-nominal conditions | PMS
Provides display data to MCR | DAS
Provides emergency letdown | RCS
Provides flow coastdown on loss of power | RCS
Provides heat removal during design basis event | PXS
Provides heat removal for RCS | SGS
Provides manual reactor trip and safety system actuation | PMS
Provides overpressure protection | RCS
Provides overpressure protection | SGS
Provides overspeed protection | RCS
Provides passive recirculation flow within MCR | VES
Provides path for water makeup to PCCWST | PCS
Provides path for water makeup to spent fuel pool | PCS
Provides pH adjustment during DBEs | PXS
Provides remote operation of valves | OCS
Provides storage and retrieval of historical data | DHS
Restricts feedwater flow to steam generator during DBEs | SGS
Sounds alarms, provides visual alerts | DDS
Supports manual initiation of reactor trip | DAS
Supports RCS during DBEs | PXS
Wets exterior of containment vessel | PCS
Enforce network isolation | Data_Diode
Provides network connectivity | L4_FW
Provides network connectivity | DMZ_FW
Provides network connectivity | CorpNet
Provides network connectivity | OpsNet
Provides network connectivity | SCADANet
Provides access | RU01
Provides access | TP01
Provides access | Data_Diode
Provides access | CP01

## SYSTEM
SYSTEMNAME | Description | LEVEL | ZONE | CRITICALITY | Notes | More
PXS | Passive Core Cooling System | 1 | AA | sys MC | The passive core cooling system (PXS) provides emergency core cooling during design basis events.
RCS | Reactor Coolant System | 2 | AC | sys MC | The reactor coolant system (RCS) removes heat from the reactor core and transfers it to the secondary side of the steam generators for power generation. The RCS contains two vertical U-tube steam generators, four sealless reactor coolant pumps (RCPs), and one pressurizer. | Component architecture includes steam generators reactor coolant pumps and the pressurizer. Remotely operated valves can be controlled from the MCR (main control room).
CNS | Containment System | 1 | AE | sys MC | The containment system (CNS) is the collection of boundaries that separates the containment atmosphere from the outside environment during design basis accidents.
PCS | Passive Cotainment Cooling System | 1 | AF | sys MC | The passive containment cooling system (PCS) removes heat from the containment during design basis events.
SGS | Steam Generator System | 1 | AG | sys MC | The steam generator system (SGS) and portions of the main and startup feedwater system (FWS) transport and control feedwater from the condensate system to the steam generators during normal operation. The SGS and portions of the main steam system (MSS) and turbine system (MTS) transport and control steam from the steam generators to the turbine generator during normal operations. These systems also isolates the steam generators from the turbine generator and the condensate system during design basis accidents.
VES | Main Control Room Emergency Hability System | 1 | AH | sys MC | The main control room emergency habitability system (VES) provides a supply of breathable air for the main control room (MCR) occupants and maintains the MCR at a positive pressure with respect to the surrounding areas whenever ac power is not available to operate the nuclear island nonradioactive ventilation system (VBS) or high radioactivity is detected in the MCR air supply. The VES also limits the heatup of the MCR, the 1E instrumentation and control (I&C) equipment rooms, and the Class 1E dc equipment rooms by using the heat capacity of surrounding structures. | Component descripion includes air tanks and remotely operated valves to manage air flow.
DAS | Diverse Actuation system | 2 | AJ | sys MC | The diverse actuation system (DAS) initiates reactor trip, actuates selected functions, and provides plant information to the operator. | Component description does not identify specific components. DAS process server included in components list.
PMS | Protection and Safety Monitoring System | 1 | AK | sys MC | The protection and safety monitoring system (PMS) initiates reactor trip and actuation of engineered safety features in response to plant conditions monitored by process instrumentation and provides safety-related displays. The PMS has four divisions of Reactor Trip and Engineered Safety Features Actuation, and two divisions of safety-related post-accident parameter displays.
PLS | Plant Control System | 2 | AL | sys MC | The plant control system (PLS) provides for automatic and manual control of nonsafety-related plant components during normal and emergency plant operations. The PLS has distributed controllers and operator controls interconnected by computer data links or data highways.
DDS | Data Display and Processing System | 3 | AM | sys MC | The data display and processing system (DDS) provides nonsafety-related alarms and displays, analysis of plant data, plant data logging and historical storage and retrieval, and operational support for plant personnel. The DDS has distributed computer processors and video display units to support the data processing and display functions | Component description does not identify specific compoents. Web-based HMI capability assumed.
OCS | Operation and Control Centers System | 3 | AQ | sys MC | The operation and control centers system (OCS) is developed and implemented based upon a human factors engineering (HFE) program. The human system interface (HSI) scope includes the design of the OCS and each of the HSI resources. For the purposes of the HFE program, the OCS includes the main control room, remote shutdown workstation, the local control stations, and the associated workstations for each of these centers. Implementation of the HFE program involves the completion of the human factors engineering analyses and plans described in Tier 1 Material Section 3.2, Human Factors Engineering.
DHS | Data Historian System | 3 | AR | sys ME | A Data Historian (also known as a Process Historian or Operational Historian) is a software program that records and retrieves production and process data by time; it stores the information in a time series database that can efficiently store data with minimal disk space and fast retrieva
PSS | Physical Security System | 3 | AS | sys ME | The physical security system provides physical features to detect, delay, assist response to, and defend against the design basis threat (DBT) for radiological sabotage. The physical security system consists of physical barriers and an intrusion detection system.
Data_Diode | Data diode device | 3 | NA | sys MC | Systems providing enterprise network infrastructure
L4_FW | Corporate Firewall | 4 | NB | sys ME
DMZ_FW | DMZ Firewall | 5 | NC | sys MS
CorpNet | Corporate Network Router | 4 | ND | sys ME
OpsNet | Operations Network Router | 3 | NE | sys MC
SCADANet | Supervisory Control Network Router | 2 | NF | sys MC
RU01 | Remote user system | 5 | XA | sys MS | Systems providing user access to enterprise environment
TP01 | Trusted partner system | 5 | XB | sys ME
CP01 | Corporate user system | 4 | CA | sys ME

## CTYPE
CTYPEID | Vendor | Description | Type | Platform | Notes
C001 | Dell | PowerEdge R440 | Server | Linux | Generic Linux system
C002 | Dell | PowerEdge R440 | Server | Windows | Generic Windows system
C003 | Cisco | CGR 2010 | Router | Linux | Generic IP router (industrial use)
C004 | Cisco | 2500 | Switch | Linux | Generic Ethernet switch
C005 | Ovation | OCR1100 | Controller | ICS | https://www.emerson.com/documents/automation/ovation-controller-model-ocr1100-en-67350.pdf
C006 | Emerson | RXi2-XP | Server | Linux | https://www.emerson.com/en-us/catalog/automation-solutions/control-safety-systems/industrial-pc-ipc/emerson-r2x0n1r0b1t0a
C007 | Moxa | Mgate 5111 | Protocol Gateway | Linux | https://www.moxa.com/en/products/industrial-edge-connectivity/protocol-gateways/fieldbus-gateways/mgate-5111-series
C008 | Emerson | TopWorx | Controller | ICS | https://www.emerson.com/documents/automation/brochure-topworx-discrete-valve-controllers-product-topworx-en-82560.pdf
C009 | Siemens | S7-1500 | Controller | ICS | https://new.siemens.com/global/en/products/automation/systems/industrial/plc/simatic-s7-1500.html
C010 | GE Digital | Web HMI | HMI | Windows | https://www.ge.com/digital/sites/default/files/download_assets/Web-HMI-2-dot-2-from-ge-digital-datasheet.pdf
C011 | TRESYS | XDBridge | Data Diode | Linux | https://www.tresys.com/application/files/8215/5533/9863/Tresys_XDBridge_Sheet.pdf

## COMPONENT
COMPONENTID | CTYPEID | ASSET NAME | SYSTEM NAME | CRITICALITY | Description/Notes
RCS01 | C005 | RCS-MP-01A | RCS | comp MC | Controller for Reactor Coolant Pump (RCP) 1A
RCS02 | C005 | RCS-MP-01B | RCS | comp MC | Controller for RCP 1B
RCS03 | C005 | RCS-MP-02A | RCS | comp MC | Controller for RCP 2A
RCS04 | C005 | RCS-MP-02B | RCS | comp MC | Controller for RCP 2B
RCS05 | C008 | RCS-MV-02 | RCS | comp MC | Controller for Pressurizer heater
RCS06 | C008 | RCS-PL-V001A | RCS | comp MC | Controller for First-stage Automatic Depressurization System (ADS) Motor-operated Valve (MOV)
RCS07 | C008 | RCS-PL-V002A | RCS | comp MC | Controller for Second-stage ADS MOV
RCS08 | C008 | RCS-PL-V010A | RCS | comp MC | Controller for ADS Discharge Header A Vacuum Relief Valve
RCS09 | C008 | RCS-PL-V010B | RCS | comp MC | Controller for ADS Discharge Header B Vacuum Relief Valve
RCS10 | C008 | RCS-PL-V011A | RCS | comp MC | Controller for First-stage ADS Isolation MOV
RCS11 | C008 | RCS-PL-V012A | RCS | comp MC | Controller for Second-stage ADS Isolation MOV
RCS12 | C008 | RCS-PL-V150A | RCS | comp MC | Controller for Reactor Vessel Head Vent Valve
RCS13 | C006 | RCS-Processor | RCS | comp MC | Controller for Processor hosting RCS control logic: ADS
CNS01 | C009 | CAS-PL-V014 | CNS | comp MC | Controller for Instrument Air Supply Outside Containment Isolation Valve
CNS02 | C009 | CCS-PL-V200 | CNS | comp MC | Controller for Cooling Water System (CCS) Containment Isolation Motor-operated Valve (MOV) – Inlet Line Outside Reactor Containment (ORC)
CNS03 | C009 | CCS-PL-V207 | CNS | comp MC | Controller for CCS Containment Isolation MOV – Outlet Line IRC
CNS04 | C009 | CCS-PL-V208 | CNS | comp MC | Controller for CCS Containment Isolation MOV – Outlet Line ORC
CNS05 | C005 | SFS-PL-V038 | CNS | comp MC | Controller for SFS Discharge Line Containment Isolation MOV – ORC
CNS06 | C005 | SFS-PL-V034 | CNS | comp MC | Controller for SFS Suction Line Containment Isolation MOV – IRC
CNS07 | C005 | SFS-PL-V035 | CNS | comp MC | Controller for SFS Suction Line Containment Isolation MOV – ORC
CNS08 | C008 | VFS-PL-V003 | CNS | comp MC | Controller for Containment Purge Inlet Containment Isolation Valve – ORC
CNS09 | C008 | VFS-PL-V004 | CNS | comp MC | Controller for Containment Purge Inlet Containment Isolation Valve – IRC
CNS10 | C008 | VFS-PL-V009 | CNS | comp MC | Controller for Containment Purge Discharge Containment Isolation Valve – IRC
CNS11 | C008 | VFS-PL-V010 | CNS | comp MC | Controller for Containment Purge Discharge Containment Isolation Valve – ORC
CNS12 | C008 | VFS-PL-V800A | CNS | comp MC | Controller for Vacuum Relief Containment Isolation A – ORC
CNS13 | C008 | VFS-PL-V800B | CNS | comp MC | Controller for Vacuum Relief Containment Isolation B – ORC
CNS14 | C009 | VWS-PL-V082 | CNS | comp MC | Controller for Fan Coolers Return Containment Isolation Valve – IRC
CNS15 | C009 | VWS-PL-V086 | CNS | comp MC | Controller for Fan Coolers Return Containment Isolation Valve – ORC
CNS16 | C009 | VWS-PL-V058 | CNS | comp MC | Controller for Fan Coolers Supply Containment Isolation Valve – ORC
CNS17 | C009 | WLS-PL-V067 | CNS | comp MC | Controller for Reactor Coolant Drain Tank (RCDT) Gas Outlet Containment Isolation Valve – IRC
CNS18 | C009 | WLS-PL-V068 | CNS | comp MC | Controller for RCDT Gas Outlet Containment Isolation Valve – ORC
CNS19 | C009 | WLS-PL-V055 | CNS | comp MC | Controller for Sump Discharge Containment Isolation Valve – IRC
CNS20 | C009 | WLS-PL-V057 | CNS | comp MC | Controller for Sump Discharge Containment Isolation Valve – ORC
PCS01 | C005 | PCS-PL-V001A | PCS | comp MC | Controller for passive containment cooling water storage tank (PCCWST) Isolation Valve
PCS02 | C005 | PCS-PL-V002A | PCS | comp MC | Controller for PCCWST Isolation Block MOV
VES01 | C008 | VES-PL-V005A | VES | comp MC | Controller for MCR Air Delivery Isolation Valve A
VES02 | C008 | VES-PL-V005B | VES | comp MC | Controller for MCR Air Delivery Isolation Valve B
VES03 | C008 | VES-PL-V022A | VES | comp MC | Controller for MCR Pressure Relief Isolation Valve A
VES04 | C008 | VES-PL-V022B | VES | comp MC | Controller for MCR Pressure Relief Isolation Valve B
DAS01 | C006 | DAS-Processor | DAS | comp MC | Processor for hosting DAS control logic: automatic reactor trip
DDS01 | C010 | DDS-HMI | DDS | comp MC | HMI supporting DDS-HMI functions
PCS01 | C009 | PCS-PL-V001A | PCS | comp MC | Controller for passive containment cooling water storage tank (PCCWST) Isolation Valve
PCS02 | C009 | PCS-PL-V002A | PCS | comp MC | Controller for PCCWST Isolation Block MOV
PXS01 | C005 | PXS-PL-V002A | PXS | comp MC | Controller for CMT A Inlet Isolation Motor-operated Valve
PXS02 | C005 | PXS-PL-V014A | PXS | comp MC | Controller for CMT A Discharge Isolation Valve
PXS03 | C005 | PXS-PL-V027A | PXS | comp MC | Controller for Accumulator A Discharge Isolation Valve
PXS04 | C005 | PXS-PL-V042 | PXS | comp MC | Controller for Nitrogen Supply Containment Isolation Valve
PXS05 | C005 | PXS-PL-V101 | PXS | comp MC | Controller for PRHR HX Inlet Isolation Motor-operated Valve
PXS06 | C005 | PXS-PL-V108A | PXS | comp MC | Controller for PRHR HX Control Valve
PXS07 | C005 | PXS-PL-V117A | PXS | comp MC | Controller for Containment Recirculation A Isolation Motor-operated Valve
PXS08 | C009 | PXS-PL-V118A | PXS | comp MC | Controller for Containment Recirculation A Squib Valve
PXS09 | C005 | PXS-PL-V120A | PXS | comp MC | Controller for Containment Recirculation A Squib Valve
PXS10 | C005 | PXS-PL-V123A | PXS | comp MC | Controller for IRWST Injection A Squib Valve
PXS11 | C005 | PXS-PL-V125A | PXS | comp MC | Controller for IRWST Injection A Squib Valve
PXS12 | C005 | PXS-PL-V130A | PXS | comp MC | Controller for IRWST Gutter Isolation Valve
SGS01 | C008 | SGS-PL-V027A | SGS | comp MC | Controller for Power-operated Relief Valve Block Motor-operated Valve Steam Generator 01
SGS02 | C008 | SGS-PL-V036A | SGS | comp MC | Controller for Steam Line Condensate Drain Isolation Valve
SGS03 | C008 | SGS-PL-V040A | SGS | comp MC | Controller for Main Steam Line Isolation Valve
SGS04 | C008 | SGS-PL-V086A | SGS | comp MC | Controller for Steam Line Condensate Drain Control Valve
SGS05 | C008 | SGS-PL-V057A | SGS | comp MC | Controller for Main Feedwater Isolation Valve
SGS06 | C008 | SGS-PL-V067A | SGS | comp MC | Controller for Startup Feedwater Isolation Motor-operated Valve
SGS07 | C008 | SGS-PL-V074A | SGS | comp MC | Controller for Steam Generator Blowdown Isolation Valve
SGS08 | C008 | SGS-PL-V075A | SGS | comp MC | Controller for Steam Generator Blowdown Isolation Valve
SGS09 | C008 | SGS-PL-V233A | SGS | comp MC | Controller for Power-operated Relief Valve
SGS10 | C008 | SGS-PL-V240A | SGS | comp MC | Controller for Main Steam Isolation Valve Bypass Isolation
SGS11 | C008 | SGS-PL-V250A | SGS | comp MC | Controller for Main Feedwater Control Valve
SGS12 | C008 | SGS-PL-V255A | SGS | comp MC | Controller for Startup Feedwater Control Valve
PMS02 | C006 | PMS02 | PMS | comp MC | Server for Reactor Trip Switchgear
PMS03 | C006 | PMS03 | PMS | comp MC | Server for MCR/RSW Transfer Panels
PMS04 | C010 | PMS04 | PMS | comp MC | HMI for MCR Displays
PMS05 | C006 | PMS05 | PMS | comp MC | Server for MCR Safety-Related Controls
OCS02 | C001 | OCS02 | OCS | comp MC | Workstation - Remote Shutdown Workstation
OCS07 | C010 | OCS07 | OCS | comp MC | HMI for Remote Shutdown Workstation
OCS03 | C001 | OCS03 | OCS | comp MC | Workstation - Local Control Station 1
OCS04 | C001 | OCS04 | OCS | comp MC | Workstation - Local Control Station 2
OCS05 | C001 | OCS05 | OCS | comp MC | Workstation 1
OCS06 | C001 | OCS06 | OCS | comp MC | Workstation 2
NT001 | C011 | Data_Diode | Data_Diode | comp MC
NT002 | C003 | L4_FW | L4_FW | comp ME
NT003 | C003 | DMZ_FW | DMZ_FW | comp MS
NT004 | C004 | OpsNet | OpsNet | comp MC
NT005 | C004 | SCADANet | SCADANet | comp MC
NT006 | C004 | CorpNet | CorpNet | comp ME
EX001 | C002 | Remote_User_Laptop | RU01 | comp MS
EX002 | C002 | Trusted_Partner_Laptop | TP01 | comp ME
NT007 | C002 | Corporate_User_Laptop | CP01 | comp ME

## CONNECTION
Source System | Dest System | Flow | Unused | Unused | Unused
RU01 | DMZ_FW | bothway | A | C003 | 0
TP01 | DMZ_FW | bothway | B | C003 | 0
DMZ_FW | CorpNet | bothway | C | C003 | 0
CorpNet | L4_FW | bothway | X | C003 | 0
CorpNet | CP01 | bothway | D | C003 | 0
DMZ_FW | L4_FW | bothway | E | C003 | 0
L4_FW | Data_Diode | bothway | G | C003 | 0
Data_Diode | OpsNet | bothway | F | C003 | 0
OpsNet | PSS | bothway | H | C003 | 0
OpsNet | DHS | bothway | J | C003 | 0
OpsNet | OCS | bothway | K | C003 | 0
Data_Diode | SCADANet | bothway | L | C003 | 0
SCADANet | RCS | bothway | M | C003 | 0
SCADANet | DAS | bothway | N | C003 | 0
SCADANet | PLS | bothway | P | C003 | 0
SCADANet | PXS | bothway | Q | C003 | 0
SCADANet | SGS | bothway | R | C003 | 0
SCADANet | PCS | bothway | S | C003 | 0
SCADANet | CNS | bothway | T | C003 | 0
SCADANet | VES | bothway | V | C003 | 0

## LOCATION
Level | Zone | Description | Owner | Access | Notes
1 | AA | Passive Core Cooling System (PXS) | Operations | Hard | Safety system
1 | AE | Containment System (CNS) | Operations | Hard | Safety system
1 | AF | Passive Cotainment Cooling System (PCS) | Operations | Hard | Safety system
1 | AG | Steam Generator System (SGS) | Operations | Hard | Safety system
1 | AH | Main Control Room Emergency Habitability System (VES) | Operations | Hard | Safety system
1 | AK | Protection and Safety Monitoring System (PMS) | Operations | Hard | Safety system
2 | AC | Reactor Coolant System (RCS) | Operations | Hard | Safety system
2 | AJ | Diverse Actuation System (DAS) | Operations | Hard | Safety system
2 | AL | Plant Control System (PLS) | Operations | Hard | Safety system
2 | NF | Supervisory Control Network Router | Operations | Hard | SCADANet
3 | AM | Data Display and Processing System (DDS) | Operations | Moderate | Instrumentation and Control (I&C)
3 | AQ | Operation and Control Centers System (OCS) | Operations | Moderate | Instrumentation and Control (I&C)
3 | AR | Data Historian System (DHS) | Operations | Moderate | Instrumentation and Control (I&C)
3 | AS | Physical Security System (PSS) | Operations | Hard | Instrumentation and Control (I&C)
3 | NA | Data diode | Operations | Moderate | Data_Diode
3 | NE | Operations Network Router | Operations | Moderate | OpsNet
4 | NB | Corporate Firewall | Corporate | Moderate | L4_FW
4 | ND | Corporate Network Router | Corporate | Moderate | CorpNet
4 | CA | Corporate user system | Corporate | Moderate | CP01
5 | NC | DMZ Firewall | Operations | Moderate | DMZ_FW
5 | XA | Remote user system | Corporate | Easy | RU01
5 | XB | Trusted partner system | Corporate | Moderate | TP01

## SURFACE
MASTER
IDE
port
\.Net
access control
Access Control List
access point
account
active directory
activeX
actuator
admin
Adobe
advertising link
air-gap
alarm
analog signal
android.os.Build
API
ARP
ASCII
authorized app store
background
Background Intelligent Transfer Service
Base64
BIOS
blacklist
bluetooth
BOOT_COMPLETED
bootloader
browser
cache
camera
cellular
certificate authority
channel
character encoding
charging station
Citrix
CLI
cloud
command message
command-line
Component Object Model
connection proxy
contractor
control device
control logic
control protocol
control server
control software
control system
controller
credential
cron
crypto
database
default credential
digital signature
directory
discretionary access control list
DLL
DNS
domain controller
Domain Name Service
driver
dual-homed
dylib
Dynamic Data Exchange
equipment
ethernet
firewall
firmware
Flash
gateway
global positioning system
GPS
Graphical User Interface
GSM
GUI
HBSS
hidden
high volume
HISTCONTROL
historian
HMI
host
HTTP proxy
HTTPS
hypervisor
I/O
ICMP
ICS
industrial operation
industrial protocol
input image table
InstallUtil
Integrated Development Environment
Internet Control Message Protocol
Internet-facing
interpreter
inter-process communication
javascript
Kerberos
kernel
kernel-mode
ladder logic
Loadable Kernel Modules
lockscreen
LTE
machine
manual
MIME
modbus
modem
motor
Mshta.exe
named pipe
network connection
network interface
network share
NTDLL.dll
Oauth
Object Linking and Embedding
Office
operating mode
operating system
operational information
operator
OT network
packet size
passcode
password
peripheral device
physical process
PLC
policy
POU
predefined account
process
process control
process environment
process state
process variable
processing board
Program Organizational Unit
programmable
programming error
protection function
protection relay
public-facing application
pump
radio
rc\.common
RDP
Regasm
registry
Regsvcs
remote
Remote access
remote server
remote service
removable media
reporting message
RPC
RTU
rule
rundll32.exe
sandbox
SCCM
screen capture
screensaver
scripting language
secret key
Secure shell
Security Accounts Manager
security identifier
sensor
serial COM
serial connection
serially connected
service
session
shell
shim
SIEM
SIM card
smart card
SMB
SMS
SMTP
SNMP
SQL
SS7
SSH
Subject Interface Package
sudo
supplier
supply chain
system partition
TCP
telnet
third party service
thread
TLS
traffic
Trap
Trusted Execution Environment
trusted third part
tunnel
UDP
Unicode
update feature
update mode
USB device
User Datagram Protocol
user interaction
UTF-8
utility
valve
VBScript
virtual
virus signature
VNC
VPN
web
web browser
web server
webmail
Wi-Fi
WinDbg
Windows
Windows Management Instrumentation
Windows Native API
Windows Transactional NTFS
Winlogon.exe
wireless
workstation
XML
XSL